## ISO Curve
2Pole (2900 Rpm)
Model | Impeller Max | Impeller 2 | Impeller 3 | Impeller 4 | Impeller 5 | Impeller 6 | Impeller Min | Multiplier | Flow 1 | Flow 2 | Flow 3 | Flow 4 | Flow 5 | Flow 6 | Flow 7 | Flow 8 | Flow 9 | Flow 10 | Flow 11 | Flow 12 | Flow 13 | Flow 14 | Flow 15 | Flow 16 | Flow 17 | Flow 18 | Flow 19 | Flow 20 | Head 1 | Head 2 | Head 3 | Head 4 | Head 5 | Head 6 | Head 7 | Head 8 | Head 9 | Head 10 | Head 11 | Head 12 | Head 13 | Head 14 | Head 15 | Head 16 | Head 17 | Head 18 | Head 19 | Head 20 | NPSH 1 | NPSH 2 | NPSH 3 | NPSH 4 | NPSH 5 | NPSH 6 | NPSH 7 | NPSH 8 | NPSH 9 | NPSH 10 | NPSH 11 | NPSH 12 | NPSH 13 | NPSH 14 | NPSH 15 | NPSH 16 | NPSH 17 | NPSH 18 | NPSH 19 | NPSH 20 | Imp A - 1 | Imp A - 2 | Imp A - 3 | Imp A - 4 | Imp A - 5 | Imp A - 6 | Imp A - 7 | Imp A - 8 | Imp A - 9 | Imp A - 10 | Imp A - 11 | Imp A - 12 | Imp A - 13 | Imp A - 14 | Imp A - 15 | Imp A - 16 | Imp A - 17 | Imp A - 18 | Imp A - 19 | Imp A - 20 | Imp B - 1 | Imp B - 2 | Imp B - 3 | Imp B - 4 | Imp B - 5 | Imp B - 6 | Imp B - 7 | Imp B - 8 | Imp B - 9 | Imp B - 10 | Imp B - 11 | Imp B - 12 | Imp B - 13 | Imp B - 14 | Imp B - 15 | Imp B - 16 | Imp B - 17 | Imp B - 18 | Imp B - 19 | Imp B - 20 | Imp C - 1 | Imp C - 2 | Imp C - 3 | Imp C - 4 | Imp C - 5 | Imp C - 6 | Imp C - 7 | Imp C - 8 | Imp C - 9 | Imp C - 10 | Imp C - 11 | Imp C - 12 | Imp C - 13 | Imp C - 14 | Imp C - 15 | Imp C - 16 | Imp C - 17 | Imp C - 18 | Imp C - 19 | Imp C - 20 | Imp D - 1 | Imp D - 2 | Imp D - 3 | Imp D - 4 | Imp D - 5 | Imp D - 6 | Imp D - 7 | Imp D - 8 | Imp D - 9 | Imp D - 10 | Imp D - 11 | Imp D - 12 | Imp D - 13 | Imp D - 14 | Imp D - 15 | Imp D - 16 | Imp D - 17 | Imp D - 18 | Imp D - 19 | Imp D - 20 | Imp E - 1 | Imp E - 2 | Imp E - 3 | Imp E - 4 | Imp E - 5 | Imp E - 6 | Imp E - 7 | Imp E - 8 | Imp E - 9 | Imp E - 10 | Imp E - 11 | Imp E - 12 | Imp E - 13 | Imp E - 14 | Imp E - 15 | Imp E - 16 | Imp E - 17 | Imp E - 18 | Imp E - 19 | Imp E - 20 | Imp F - 1 | Imp F - 2 | Imp F - 3 | Imp F - 4 | Imp F - 5 | Imp F - 6 | Imp F - 7 | Imp F - 8 | Imp F - 9 | Imp F - 10 | Imp F - 11 | Imp F - 12 | Imp F - 13 | Imp F - 14 | Imp F - 15 | Imp F - 16 | Imp F - 17 | Imp F - 18 | Imp F - 19 | Imp F - 20 | Imp G - 1 | Imp G - 2 | Imp G - 3 | Imp G - 4 | Imp G - 5 | Imp G - 6 | Imp G - 7 | Imp G - 8 | Imp G - 9 | Imp G - 10 | Imp G - 11 | Imp G - 12 | Imp G - 13 | Imp G - 14 | Imp G - 15 | Imp G - 16 | Imp G - 17 | Imp G - 18 | Imp G - 19 | Imp G - 20 | RPM
50-32-160 | [8 empty] | NPSH 20: 100
50-32-200 | 228 | 217 | 205 | 194 | 182 | 182 | 182 | 2 | 0 | 1 | 2 | 3 | 3 | 3 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 69.3 | 69.2 | 69.1 | 69 | 69 | 69 | 69 | 68.8 | 67.8 | 66 | 62.8 | 56.3 | 48.8 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1.4 | 1.5 | 1.6 | 1.7 | 1.7 | 1.7 | 1.7 | 1.8 | 1.9 | 2 | 2.3 | 2.8 | 3.3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 18 | 28 | 37 | 37 | 37 | 37 | 43 | 48 | 52.5 | 55 | 53 | 50 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 0 | 17 | 27 | 36 | 36 | 36 | 36 | 42 | 47 | 51.5 | 54 | 52 | 49 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 0 | 16 | 26 | 35 | 35 | 35 | 35 | 41 | 46 | 50.5 | 53 | 51 | 48 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 0 | 15 | 25 | 34 | 34 | 34 | 34 | 40 | 45 | 49.5 | 52 | 50 | 47 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 14 | 24 | 33 | 33 | 33 | 33 | 39 | 44 | 48.5 | 51 | 49 | 46 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 0 | 14 | 24 | 33 | 33 | 33 | 33 | 39 | 44 | 48.5 | 51 | 49 | 46 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 0 | 14 | 24 | 33 | 33 | 33 | 33 | 39 | 44 | 48.5 | 51 | 49 | 46 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 2900
65-40-200 | [8 empty] | NPSH 20: 100
65-40-250 | 278 | 264 | 250 | 236 | 222 | 222 | 222 | 1.8 | 0 | 2 | 4 | 4 | 4 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 105.6 | 105.5 | 105.3 | 105.3 | 105.3 | 105.3 | 105.1 | 104 | 101.3 | 96.3 | 88.3 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 2.2 | 2.3 | 2.4 | 2.4 | 2.4 | 2.4 | 2.6 | 2.8 | 3 | 3.5 | 5.3 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 0 | 19 | 31 | 31 | 31 | 31 | 43 | 50.5 | 55.5 | 59.5 | 56 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 0 | 18 | 30 | 30 | 30 | 30 | 42 | 49.5 | 54.5 | 58.5 | 55 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 16 | 28 | 28 | 28 | 28 | 40 | 47.5 | 52.5 | 56.5 | 53 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 0 | 15 | 27 | 27 | 27 | 27 | 39 | 46.5 | 51.5 | 55.5 | 52 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 0 | 14 | 26 | 26 | 26 | 26 | 38 | 45.5 | 50.5 | 54.5 | 51 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 0 | 14 | 26 | 26 | 26 | 26 | 38 | 45.5 | 50.5 | 54.5 | 51 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 0 | 14 | 26 | 26 | 26 | 26 | 38 | 45.5 | 50.5 | 54.5 | 51 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 2900
65-40-315 | [8 empty] | NPSH 20: 100
65-50-160 | 182 | 173 | 164 | 155 | 146 | 146 | 146 | 2 | 0 | 2 | 4 | 4 | 4 | 4 | 4 | 6 | 8 | 10 | 12 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 44.8 | 45.2 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5 | 44.5 | 43 | 40 | 35.5 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 1.6 | 1.65 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.8 | 1.9 | 2 | 3.3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 38 | 52 | 52 | 52 | 52 | 52 | 61 | 67.5 | 72 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 37 | 51 | 51 | 51 | 51 | 51 | 60 | 66.5 | 71 | 69 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 0 | 34.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 57.5 | 64 | 68.5 | 66.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 0 | 32 | 46 | 46 | 46 | 46 | 46 | 55 | 61.5 | 66 | 64 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 0 | 28.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 51.5 | 58 | 62.5 | 60.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 0 | 28.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 51.5 | 58 | 62.5 | 60.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 0 | 28.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 51.5 | 58 | 62.5 | 60.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 2900
80-50-200 | 228 | 217 | 205 | 194 | 182 | 182 | 182 | 2.15 | 0 | 2.5 | 5 | 5 | 5 | 5 | 5 | 7.5 | 10 | 12.5 | 15 | 17.5 | 20 | 22.5 | 25 | 27.5 | 30 | 30 | 30 | 30 | 74.3 | 74.2 | 74 | 74 | 74 | 74 | 74 | 73.8 | 73.6 | 73.4 | 72.8 | 71 | 68.8 | 65.8 | 61 | 58.8 | 46 | 46 | 46 | 46 | 0.9 | 0.95 | 1 | 1 | 1 | 1 | 1 | 1.1 | 1.2 | 1.4 | 1.6 | 1.8 | 2 | 2.2 | 2.5 | 2.8 | 3.1 | 3.1 | 3.1 | 3.1 | 0 | 28 | 42 | 42 | 42 | 42 | 42 | 51 | 60 | 65 | 69 | 73 | 76 | 76.3 | 73.8 | 68.3 | 60 | 60 | 60 | 60 | 0 | 27 | 41 | 41 | 41 | 41 | 41 | 50 | 59 | 64 | 68 | 72 | 75 | 75.3 | 72.8 | 67.3 | 59 | 59 | 59 | 59 | 0 | 25 | 39 | 39 | 39 | 39 | 39 | 48 | 57 | 62 | 66 | 70 | 73 | 73.3 | 70.8 | 65.3 | 57 | 57 | 57 | 57 | 0 | 22 | 36 | 36 | 36 | 36 | 36 | 45 | 54 | 59 | 63 | 67 | 70 | 70.3 | 67.8 | 62.3 | 54 | 54 | 54 | 54 | 0 | 19 | 33 | 33 | 33 | 33 | 33 | 42 | 51 | 56 | 60 | 64 | 67 | 67.3 | 64.8 | 59.3 | 51 | 51 | 51 | 51 | 0 | 19 | 33 | 33 | 33 | 33 | 33 | 42 | 51 | 56 | 60 | 64 | 67 | 67.3 | 64.8 | 59.3 | 51 | 51 | 51 | 51 | 0 | 19 | 33 | 33 | 33 | 33 | 33 | 42 | 51 | 56 | 60 | 64 | 67 | 67.3 | 64.8 | 59.3 | 51 | 51 | 51 | 51 | 2900
80-50-250 | 278 | 264 | 250 | 236 | 222 | 222 | 222 | 2 | 0 | 2 | 4 | 6 | 8 | 8 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 32 | 106.3 | 106.2 | 106.1 | 106 | 105.8 | 105.8 | 105.8 | 105.6 | 105.4 | 105.2 | 105 | 104.6 | 103.8 | 101.8 | 99.6 | 97 | 93.8 | 90.8 | 87.8 | 87.8 | 2.3 | 2.4 | 2.5 | 2.6 | 2.6 | 2.6 | 2.6 | 2.7 | 2.8 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 3.5 | 3.7 | 4 | 4.3 | 5 | 5 | 0 | 18 | 23 | 33 | 45 | 45 | 45 | 48 | 53 | 60 | 63 | 65 | 67 | 68.5 | 70 | 71 | 71 | 70 | 68 | 68 | 0 | 17.5 | 22.5 | 32.5 | 44.5 | 44.5 | 44.5 | 47.5 | 52.5 | 59.5 | 62.5 | 64.5 | 66.5 | 68 | 69.5 | 70.5 | 70.5 | 69.5 | 67.5 | 67.5 | 0 | 17 | 22 | 32 | 44 | 44 | 44 | 47 | 52 | 59 | 62 | 64 | 66 | 67.5 | 69 | 70 | 70 | 69 | 67 | 67 | 0 | 16.5 | 21.5 | 31.5 | 43.5 | 43.5 | 43.5 | 46.5 | 51.5 | 58.5 | 61.5 | 63.5 | 65.5 | 67 | 68.5 | 69.5 | 69.5 | 68.5 | 66.5 | 66.5 | 0 | 16 | 21 | 31 | 43 | 43 | 43 | 46 | 51 | 58 | 61 | 63 | 65 | 66.5 | 68 | 69 | 69 | 68 | 66 | 66 | 0 | 16 | 21 | 31 | 43 | 43 | 43 | 46 | 51 | 58 | 61 | 63 | 65 | 66.5 | 68 | 69 | 69 | 68 | 66 | 66 | 0 | 16 | 21 | 31 | 43 | 43 | 43 | 46 | 51 | 58 | 61 | 63 | 65 | 66.5 | 68 | 69 | 69 | 68 | 66 | 66 | 2900
80-50-315 | [8 empty] | NPSH 20: 100
80-65-160 | [8 empty] | NPSH 20: 100
100-65-200 | 228 | 217 | 205 | 194 | 182 | 182 | 182 | 2 | 0 | 5 | 10 | 10 | 10 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 69 | 70 | 70.3 | 70.3 | 70.3 | 70.3 | 70.5 | 70.5 | 70.2 | 69.8 | 67.8 | 64.8 | 60.3 | 56 | 51 | 51 | 51 | 51 | 51 | 51 | 2.1 | 2.2 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.4 | 2.5 | 2.6 | 2.8 | 3 | 4 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 28 | 43 | 43 | 43 | 43 | 53 | 63 | 71 | 74 | 77 | 81 | 81.5 | 80 | 76 | 76 | 76 | 76 | 76 | 76 | 0 | 27.5 | 42 | 42 | 42 | 42 | 52 | 62 | 70 | 73 | 77 | 80 | 80.5 | 79 | 75 | 75 | 75 | 75 | 75 | 75 | 0 | 27 | 41 | 41 | 41 | 41 | 51 | 61 | 69 | 72 | 75 | 79 | 79.5 | 78 | 74 | 74 | 74 | 74 | 74 | 74 | 0 | 26 | 39 | 39 | 39 | 39 | 49 | 59 | 67 | 70 | 73 | 77 | 77.5 | 76 | 72 | 72 | 72 | 72 | 72 | 72 | 0 | 25 | 37 | 37 | 37 | 37 | 47 | 57 | 65 | 68 | 71 | 75 | 75.5 | 74 | 70 | 70 | 70 | 70 | 70 | 70 | 0 | 25 | 37 | 37 | 37 | 37 | 47 | 57 | 65 | 68 | 71 | 75 | 75.5 | 74 | 70 | 70 | 70 | 70 | 70 | 70 | 0 | 25 | 37 | 37 | 37 | 37 | 47 | 57 | 65 | 68 | 71 | 75 | 75.5 | 74 | 70 | 70 | 70 | 70 | 70 | 70 | 2900
100-65-250 | 278 | 264 | 250 | 236 | 222 | 222 | 222 | 2 | 0 | 5 | 10 | 10 | 10 | 10 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 56 | 56 | 56 | 56 | 106 | 105.8 | 105.5 | 105.5 | 105.5 | 105.5 | 105.5 | 105.2 | 105 | 104 | 102.3 | 100 | 96.3 | 92.3 | 87.8 | 81 | 80 | 80 | 80 | 80 | 3 | 3.05 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.6 | 3.8 | 4 | 4.5 | 5.5 | 5.6 | 5.6 | 5.6 | 5.6 | 0 | 28 | 43 | 43 | 43 | 43 | 43 | 53 | 60 | 66 | 71 | 76 | 78.5 | 79 | 78 | 71 | 70 | 70 | 70 | 70 | 0 | 27.5 | 42 | 42 | 42 | 42 | 42 | 52 | 59 | 65 | 70 | 75 | 78 | 78 | 77 | 70 | 69 | 69 | 69 | 69 | 0 | 27 | 41 | 41 | 41 | 41 | 41 | 51 | 58 | 64 | 69 | 74 | 77 | 77 | 76 | 69 | 68 | 68 | 68 | 68 | 0 | 26 | 40 | 40 | 40 | 40 | 40 | 50 | 57 | 63 | 68 | 63 | 76 | 76 | 75 | 68 | 67 | 67 | 67 | 67 | 0 | 25 | 38 | 38 | 38 | 38 | 38 | 48 | 55 | 61 | 66 | 61 | 74 | 74 | 73 | 66 | 65 | 65 | 65 | 65 | 0 | 25 | 38 | 38 | 38 | 38 | 38 | 48 | 55 | 61 | 66 | 61 | 74 | 74 | 73 | 66 | 65 | 65 | 65 | 65 | 0 | 25 | 38 | 38 | 38 | 38 | 38 | 48 | 55 | 61 | 66 | 61 | 74 | 74 | 73 | 66 | 65 | 65 | 65 | 65 | 2900
100-65-315 | 342 | 325 | 308 | 291 | 274 | 274 | 274 | 2 | 0 | 5 | 10 | 10 | 10 | 10 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 60 | 60 | 60 | 160.5 | 160.3 | 160 | 160 | 160 | 160 | 160 | 159.7 | 159.1 | 157.3 | 155.5 | 152.3 | 149.3 | 145.7 | 140 | 133.8 | 126.8 | 126.8 | 126.8 | 126.8 | 1.6 | 1.7 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.9 | 2 | 2.1 | 2.2 | 2.4 | 2.6 | 2.8 | 3 | 3.5 | 4.5 | 4.5 | 4.5 | 4.5 | 0 | 23 | 33 | 33 | 33 | 33 | 33 | 45 | 53 | 58 | 62 | 66 | 68 | 71 | 71 | 67 | 63 | 63 | 63 | 63 | 0 | 22.5 | 32 | 32 | 32 | 32 | 32 | 44 | 52 | 57 | 61 | 65 | 67 | 70 | 70 | 66 | 62.5 | 62.5 | 62.5 | 62.5 | 0 | 22 | 31 | 31 | 31 | 31 | 31 | 43 | 51 | 56 | 60 | 64 | 66 | 67 | 67 | 65 | 62 | 62 | 62 | 62 | 0 | 21 | 30 | 30 | 30 | 30 | 30 | 42 | 50 | 55 | 59 | 63 | 65 | 66 | 66 | 64 | 61 | 61 | 61 | 61 | 0 | 20 | 29 | 29 | 29 | 29 | 29 | 40 | 48 | 53 | 57 | 61 | 63 | 64 | 64 | 62 | 59 | 59 | 59 | 59 | 0 | 20 | 29 | 29 | 29 | 29 | 29 | 40 | 48 | 53 | 57 | 61 | 63 | 64 | 64 | 62 | 59 | 59 | 59 | 59 | 0 | 20 | 29 | 29 | 29 | 29 | 29 | 40 | 48 | 53 | 57 | 61 | 63 | 64 | 64 | 62 | 59 | 59 | 59 | 59 | 2900
100-65-315s | 350 | 343 | 322 | 322 | 322 | 322 | 322 | 2.35 | 0 | 4 | 8 | 12 | 16 | 20 | 24 | 24 | 28 | 32 | 36 | 40 | 44 | 48 | 52 | 56 | 56 | 56 | 56 | 56 | 175 | 174.5 | 174 | 173.5 | 173 | 172 | 171 | 171 | 168 | 163.5 | 158 | 151 | 142 | 133 | 118 | 100 | 100 | 100 | 100 | 100 | 3.1 | 3.2 | 3.25 | 3.3 | 3.4 | 3.5 | 3.7 | 3.7 | 4 | 4.4 | 4.9 | 5.5 | 6.2 | 6.8 | 8 | 10 | 10 | 10 | 10 | 10 | 0 | 18 | 33 | 42 | 51 | 57 | 61.5 | 61.5 | 64.7 | 66 | 67.5 | 68 | 67 | 65 | 59 | 53 | 53 | 53 | 53 | 53 | 0 | 17.5 | 32.5 | 41.5 | 50.5 | 56.5 | 61.5 | 61.5 | 64 | 65 | 66.5 | 67 | 66 | 64 | 58 | 52 | 52 | 52 | 52 | 52 | 0 | 17 | 32 | 41 | 50 | 56 | 61 | 61 | 63 | 64 | 65.5 | 66 | 65 | 63 | 57 | 51 | 51 | 51 | 51 | 51 | 0 | 17 | 32 | 41 | 50 | 56 | 61 | 61 | 63 | 64 | 65.5 | 66 | 65 | 63 | 57 | 51 | 51 | 51 | 51 | 51 | 0 | 17 | 32 | 41 | 50 | 56 | 61 | 61 | 63 | 64 | 65.5 | 66 | 65 | 63 | 57 | 51 | 51 | 51 | 51 | 51 | 0 | 17 | 32 | 41 | 50 | 56 | 61 | 61 | 63 | 64 | 65.5 | 66 | 65 | 63 | 57 | 51 | 51 | 51 | 51 | 51 | 0 | 17 | 32 | 41 | 50 | 56 | 61 | 61 | 63 | 64 | 65.5 | 66 | 65 | 63 | 57 | 51 | 51 | 51 | 51 | 51 | 2900
100-80-160 | 182 | 173 | 164 | 155 | 146 | 146 | 146 | 2 | 0 | 5 | 10 | 10 | 10 | 10 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 55 | 55 | 55 | 43.3 | 43.2 | 43.1 | 43.1 | 43.1 | 43.1 | 43.1 | 42.9 | 42 | 41 | 39 | 37.2 | 34.3 | 31 | 26.5 | 21 | 21 | 21 | 21 | 21 | 2.5 | 2.6 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.8 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 3.8 | 5.8 | 8 | 8 | 8 | 8 | 8 | 0 | 28 | 43 | 43 | 43 | 43 | 43 | 58 | 70 | 76 | 78.3 | 80.3 | 80.3 | 78.5 | 72.3 | 58 | 58 | 58 | 58 | 58 | 0 | 27 | 42 | 42 | 42 | 42 | 42 | 57 | 69 | 75 | 78.3 | 79.3 | 79.3 | 77.5 | 71.3 | 57 | 57 | 57 | 57 | 57 | 0 | 26 | 41 | 41 | 41 | 41 | 41 | 56 | 68 | 74 | 76.3 | 78.3 | 78.3 | 76.5 | 70.3 | 56 | 56 | 56 | 56 | 56 | 0 | 24.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 54.2 | 66.2 | 72.2 | 74.5 | 76.5 | 76.5 | 74.7 | 68.5 | 54.2 | 54.2 | 54.2 | 54.2 | 54.2 | 0 | 21.4 | 36.4 | 36.4 | 36.4 | 36.4 | 36.4 | 51.4 | 63.4 | 69.4 | 71.7 | 73.7 | 73.7 | 71.9 | 65.7 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 0 | 21.4 | 36.4 | 36.4 | 36.4 | 36.4 | 36.4 | 51.4 | 63.4 | 69.4 | 71.7 | 73.7 | 73.7 | 71.9 | 65.7 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 0 | 21.4 | 36.4 | 36.4 | 36.4 | 36.4 | 36.4 | 51.4 | 63.4 | 69.4 | 71.7 | 73.7 | 73.7 | 71.9 | 65.7 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 2900
125-100-200 | 228 | 217 | 205 | 194 | 182 | 182 | 182 | 2.35 | 0 | 10 | 20 | 30 | 30 | 30 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 108 | 108 | 108 | 108 | 108 | 108 | 67.9 | 67.6 | 67.3 | 67 | 67 | 67 | 67 | 66 | 65 | 63 | 60 | 57 | 53 | 46 | 38 | 38 | 38 | 38 | 38 | 38 | 2.95 | 3 | 3.05 | 3.1 | 3.1 | 3.1 | 3.1 | 3.2 | 3.4 | 3.6 | 3.9 | 4.2 | 4.6 | 5.3 | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 23 | 45 | 53 | 53 | 53 | 53 | 67 | 76 | 80 | 83.3 | 85.2 | 84.8 | 82 | 77 | 77 | 77 | 77 | 77 | 77 | 0 | 22 | 44 | 52 | 52 | 52 | 52 | 66 | 75 | 79 | 82.3 | 84.2 | 83.8 | 81 | 76 | 76 | 76 | 76 | 76 | 76 | 0 | 21.5 | 43.5 | 51.5 | 51.5 | 51.5 | 51.5 | 65 | 73 | 78 | 81.3 | 83.2 | 82.8 | 80 | 75 | 75 | 75 | 75 | 75 | 75 | 0 | 20 | 42 | 50 | 50 | 50 | 50 | 63 | 71 | 76 | 79.3 | 81.2 | 80.8 | 78 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 0 | 18.8 | 40.8 | 48.8 | 48.8 | 48.8 | 48.8 | 61.8 | 69.5 | 74.5 | 77.5 | 79 | 78.5 | 76 | 72 | 72 | 72 | 72 | 72 | 72 | 0 | 18.8 | 40.8 | 48.8 | 48.8 | 48.8 | 48.8 | 61.8 | 69.5 | 74.5 | 77.5 | 79 | 78.5 | 76 | 72 | 72 | 72 | 72 | 72 | 72 | 0 | 18.8 | 40.8 | 48.8 | 48.8 | 48.8 | 48.8 | 61.8 | 69.5 | 74.5 | 77.5 | 79 | 78.5 | 76 | 72 | 72 | 72 | 72 | 72 | 72 | 2900
125-100-250 | 278 | 264 | 250 | 236 | 222 | 222 | 222 | 2 | 0 | 10 | 20 | 20 | 20 | 20 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 108 | 108 | 108 | 108 | 108 | 105.5 | 105.3 | 105.1 | 105.1 | 105.1 | 105.1 | 105.1 | 104.9 | 104.5 | 104 | 103 | 98 | 94 | 88 | 80 | 72 | 72 | 72 | 72 | 72 | 3.8 | 3.9 | 3.95 | 3.95 | 3.95 | 3.95 | 3.95 | 4 | 4.05 | 4.1 | 4.2 | 4.3 | 4.4 | 4.5 | 5.5 | 7 | 7 | 7 | 7 | 7 | 0 | 28 | 43 | 43 | 43 | 43 | 43 | 58 | 68 | 74.7 | 79 | 82.3 | 85 | 85 | 82 | 76 | 76 | 76 | 76 | 76 | 0 | 27 | 41 | 41 | 41 | 41 | 41 | 56 | 66 | 72 | 76 | 79.3 | 83 | 83 | 79 | 74 | 74 | 74 | 74 | 74 | 0 | 26.5 | 40 | 40 | 40 | 40 | 40 | 55 | 65 | 71 | 75 | 78 | 82 | 82 | 78 | 73 | 73 | 73 | 73 | 73 | 0 | 25.5 | 38.8 | 38.8 | 38.8 | 38.8 | 38.8 | 53.5 | 63.5 | 69.5 | 73.5 | 76.5 | 80.5 | 80.5 | 76.5 | 72 | 72 | 72 | 72 | 72 | 0 | 24.8 | 38 | 38 | 38 | 38 | 38 | 52 | 62 | 68 | 72 | 75 | 79 | 79 | 75 | 71 | 71 | 71 | 71 | 71 | 0 | 24.8 | 38 | 38 | 38 | 38 | 38 | 52 | 62 | 68 | 72 | 75 | 79 | 79 | 75 | 71 | 71 | 71 | 71 | 71 | 0 | 24.8 | 38 | 38 | 38 | 38 | 38 | 52 | 62 | 68 | 72 | 75 | 79 | 79 | 75 | 71 | 71 | 71 | 71 | 71 | 2900
125-100-315 | 342 | 325 | 308 | 291 | 274 | 274 | 274 | 2 | 0 | 10 | 20 | 20 | 20 | 20 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 113 | 113 | 113 | 113 | 162.3 | 162 | 161.7 | 161.7 | 161.7 | 161.7 | 161.7 | 161.3 | 161 | 160.5 | 159.7 | 155.8 | 150 | 144 | 135.7 | 124.8 | 120 | 120 | 120 | 120 | 2.6 | 2.7 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.9 | 3 | 3.3 | 3.6 | 3.95 | 4.3 | 4.65 | 5 | 5.4 | 6.3 | 6.3 | 6.3 | 6.3 | 0 | 25 | 41 | 41 | 41 | 41 | 41 | 54 | 65 | 73.8 | 77 | 79.5 | 83 | 84.5 | 84 | 80.5 | 78 | 78 | 78 | 78 | 0 | 24.5 | 40 | 40 | 40 | 40 | 40 | 53 | 64 | 72.8 | 76 | 78.5 | 82 | 83.5 | 83 | 79.5 | 77 | 77 | 77 | 77 | 0 | 24 | 39.5 | 39.5 | 39.5 | 39.5 | 39.5 | 52.5 | 63.5 | 72.5 | 75.5 | 78 | 81.5 | 83 | 82.5 | 79 | 76.5 | 76.5 | 76.5 | 76.5 | 0 | 23 | 38 | 38 | 38 | 38 | 38 | 51 | 62 | 71 | 74 | 76.5 | 80 | 81.5 | 81 | 77.5 | 75 | 75 | 75 | 75 | 0 | 22 | 36 | 36 | 36 | 36 | 36 | 49 | 60 | 68.5 | 71.5 | 74 | 77.5 | 79 | 78.5 | 75 | 72.5 | 72.5 | 72.5 | 72.5 | 0 | 22 | 36 | 36 | 36 | 36 | 36 | 49 | 60 | 68.5 | 71.5 | 74 | 77.5 | 79 | 78.5 | 75 | 72.5 | 72.5 | 72.5 | 72.5 | 0 | 22 | 36 | 36 | 36 | 36 | 36 | 49 | 60 | 68.5 | 71.5 | 74 | 77.5 | 79 | 78.5 | 75 | 72.5 | 72.5 | 72.5 | 72.5 | 2900
150-125-250 | 278 | 264 | 250 | 236 | 222 | 222 | 222 | 2 | 0 | 12 | 24 | 24 | 24 | 24 | 24 | 36 | 48 | 60 | 72 | 84 | 96 | 108 | 120 | 120 | 120 | 120 | 120 | 120 | 102.5 | 102.3 | 102 | 102 | 102 | 102 | 102 | 101.7 | 101.3 | 100.9 | 100.5 | 99 | 96 | 93 | 75 | 75 | 75 | 75 | 75 | 75 | 2.8 | 2.85 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 3.5 | 4 | 4.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 0 | 23 | 35 | 35 | 35 | 35 | 35 | 48 | 57 | 64 | 69 | 73 | 76.5 | 75 | 64 | 64 | 64 | 64 | 64 | 64 | 0 | 22 | 34 | 34 | 34 | 34 | 34 | 47 | 56 | 63 | 68 | 72 | 76 | 74 | 63 | 63 | 63 | 63 | 63 | 63 | 0 | 21.5 | 33.5 | 33.5 | 33.5 | 33.5 | 33.5 | 46 | 55 | 62 | 67 | 71 | 75 | 73 | 62 | 62 | 62 | 62 | 62 | 62 | 0 | 21 | 33 | 33 | 33 | 33 | 33 | 45 | 54 | 61 | 66 | 70 | 74 | 72 | 61 | 61 | 61 | 61 | 61 | 61 | 0 | 20.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 44 | 53 | 60 | 65 | 69 | 73 | 71 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 20.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 44 | 53 | 60 | 65 | 69 | 73 | 71 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 20.5 | 32.5 | 32.5 | 32.5 | 32.5 | 32.5 | 44 | 53 | 60 | 65 | 69 | 73 | 71 | 60 | 60 | 60 | 60 | 60 | 60 | 2900
4Pole (1450 Rpm)
Model | Impeller Max | Impeller 2 | Impeller 3 | Impeller 4 | Impeller 5 | Impeller 6 | Impeller Min | Multiplier | Flow 1 | Flow 2 | Flow 3 | Flow 4 | Flow 5 | Flow 6 | Flow 7 | Flow 8 | Flow 9 | Flow 10 | Flow 11 | Flow 12 | Flow 13 | Flow 14 | Flow 15 | Flow 16 | Flow 17 | Flow 18 | Flow 19 | Flow 20 | Head 1 | Head 2 | Head 3 | Head 4 | Head 5 | Head 6 | Head 7 | Head 8 | Head 9 | Head 10 | Head 11 | Head 12 | Head 13 | Head 14 | Head 15 | Head 16 | Head 17 | Head 18 | Head 19 | Head 20 | NPSH 1 | NPSH 2 | NPSH 3 | NPSH 4 | NPSH 5 | NPSH 6 | NPSH 7 | NPSH 8 | NPSH 9 | NPSH 10 | NPSH 11 | NPSH 12 | NPSH 13 | NPSH 14 | NPSH 15 | NPSH 16 | NPSH 17 | NPSH 18 | NPSH 19 | NPSH 20 | Imp A - 1 | Imp A - 2 | Imp A - 3 | Imp A - 4 | Imp A - 5 | Imp A - 6 | Imp A - 7 | Imp A - 8 | Imp A - 9 | Imp A - 10 | Imp A - 11 | Imp A - 12 | Imp A - 13 | Imp A - 14 | Imp A - 15 | Imp A - 16 | Imp A - 17 | Imp A - 18 | Imp A - 19 | Imp A - 20 | Imp B - 1 | Imp B - 2 | Imp B - 3 | Imp B - 4 | Imp B - 5 | Imp B - 6 | Imp B - 7 | Imp B - 8 | Imp B - 9 | Imp B - 10 | Imp B - 11 | Imp B - 12 | Imp B - 13 | Imp B - 14 | Imp B - 15 | Imp B - 16 | Imp B - 17 | Imp B - 18 | Imp B - 19 | Imp B - 20 | Imp C - 1 | Imp C - 2 | Imp C - 3 | Imp C - 4 | Imp C - 5 | Imp C - 6 | Imp C - 7 | Imp C - 8 | Imp C - 9 | Imp C - 10 | Imp C - 11 | Imp C - 12 | Imp C - 13 | Imp C - 14 | Imp C - 15 | Imp C - 16 | Imp C - 17 | Imp C - 18 | Imp C - 19 | Imp C - 20 | Imp D - 1 | Imp D - 2 | Imp D - 3 | Imp D - 4 | Imp D - 5 | Imp D - 6 | Imp D - 7 | Imp D - 8 | Imp D - 9 | Imp D - 10 | Imp D - 11 | Imp D - 12 | Imp D - 13 | Imp D - 14 | Imp D - 15 | Imp D - 16 | Imp D - 17 | Imp D - 18 | Imp D - 19 | Imp D - 20 | Imp E - 1 | Imp E - 2 | Imp E - 3 | Imp E - 4 | Imp E - 5 | Imp E - 6 | Imp E - 7 | Imp E - 8 | Imp E - 9 | Imp E - 10 | Imp E - 11 | Imp E - 12 | Imp E - 13 | Imp E - 14 | Imp E - 15 | Imp E - 16 | Imp E - 17 | Imp E - 18 | Imp E - 19 | Imp E - 20 | Imp F - 1 | Imp F - 2 | Imp F - 3 | Imp F - 4 | Imp F - 5 | Imp F - 6 | Imp F - 7 | Imp F - 8 | Imp F - 9 | Imp F - 10 | Imp F - 11 | Imp F - 12 | Imp F - 13 | Imp F - 14 | Imp F - 15 | Imp F - 16 | Imp F - 17 | Imp F - 18 | Imp F - 19 | Imp F - 20 | Imp G - 1 | Imp G - 2 | Imp G - 3 | Imp G - 4 | Imp G - 5 | Imp G - 6 | Imp G - 7 | Imp G - 8 | Imp G - 9 | Imp G - 10 | Imp G - 11 | Imp G - 12 | Imp G - 13 | Imp G - 14 | Imp G - 15 | Imp G - 16 | Imp G - 17 | Imp G - 18 | Imp G - 19 | Imp G - 20 | RPM
50-32-160
50-32-200
65-40-200
65-40-250
65-40-315
65-50-160
80-50-200
80-50-250
80-50-315 | 342 | 325 | 308 | 291 | 274 | 274 | 274 | 2 | 0 | 1 | 2 | 3 | 3 | 3 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 15 | 40 | 39.9 | 39.8 | 39.7 | 39.7 | 39.7 | 39.7 | 39.6 | 39.4 | 39.2 | 38.8 | 38.4 | 37.8 | 37 | 36 | 34.8 | 33.5 | 31.2 | 28.8 | 28.8 | 1 | 1.1 | 1.2 | 1.3 | 1.3 | 1.3 | 1.3 | 1.4 | 1.5 | 1.6 | 1.7 | 1.8 | 1.9 | 2 | 2.1 | 2.2 | 2.3 | 2.4 | 2.7 | 3 | 0 | 15 | 23 | 28 | 28 | 28 | 28 | 35.5 | 43 | 45.3 | 48 | 51.5 | 54.5 | 56.3 | 58 | 59 | 57.5 | 54.5 | 50 | 50 | 0 | 14 | 22 | 27 | 27 | 27 | 27 | 34.5 | 42 | 44.3 | 47 | 50.5 | 53.5 | 55.3 | 57 | 58 | 56.5 | 53.5 | 49 | 49 | 0 | 13 | 21 | 26 | 26 | 26 | 26 | 33.5 | 41 | 43.3 | 46 | 49.5 | 52.5 | 54.3 | 56 | 57 | 55.5 | 52.5 | 48 | 48 | 0 | 12 | 20 | 25 | 25 | 25 | 25 | 32.5 | 40 | 42.3 | 45 | 48.5 | 51.5 | 53.3 | 55 | 56 | 54.5 | 51.5 | 47 | 47 | 0 | 10 | 18 | 23 | 23 | 23 | 23 | 30.5 | 38 | 40.3 | 43 | 46.5 | 49.5 | 51.3 | 53 | 54 | 52.5 | 49.5 | 45 | 45 | 0 | 10 | 18 | 23 | 23 | 23 | 23 | 30.5 | 38 | 40.3 | 43 | 46.5 | 49.5 | 51.3 | 53 | 54 | 52.5 | 49.5 | 45 | 45 | 0 | 10 | 18 | 23 | 23 | 23 | 23 | 30.5 | 38 | 40.3 | 43 | 46.5 | 49.5 | 51.3 | 53 | 54 | 52.5 | 49.5 | 45 | 45 | 1450
80-65-160
100-65-200 | 228 | 217 | 205 | 194 | 182 | 182 | 182 | 2 | 0 | 2.5 | 5 | 5 | 5 | 5 | 7.5 | 10 | 12.5 | 15 | 17.5 | 20 | 22.5 | 25 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 17.8 | 17.9 | 18 | 18 | 18 | 18 | 17.8 | 17.6 | 17.3 | 16.8 | 16.3 | 15.2 | 14.2 | 13 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 2.8 | 2.85 | 2.9 | 2.9 | 2.9 | 2.9 | 2.95 | 3 | 3.1 | 3.2 | 3.3 | 3.4 | 3.6 | 3.8 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 28 | 43 | 43 | 43 | 43 | 58 | 65 | 71 | 75 | 77.5 | 77.5 | 76 | 73 | 68 | 68 | 68 | 68 | 68 | 68 | 0 | 27.5 | 42 | 42 | 42 | 42 | 57 | 64 | 70 | 74 | 77.5 | 76.5 | 75 | 72 | 67 | 67 | 67 | 67 | 67 | 67 | 0 | 27 | 41 | 41 | 41 | 41 | 56 | 63 | 69 | 73 | 75.5 | 75.5 | 74 | 71 | 66 | 66 | 66 | 66 | 66 | 66 | 0 | 26.5 | 40 | 40 | 40 | 40 | 55 | 62 | 68 | 72 | 74.5 | 74.5 | 73 | 70 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 25.5 | 38 | 38 | 38 | 38 | 53 | 60 | 66 | 70 | 72.5 | 72.5 | 71 | 68 | 63 | 63 | 63 | 63 | 63 | 63 | 0 | 25.5 | 38 | 38 | 38 | 38 | 53 | 60 | 66 | 70 | 72.5 | 72.5 | 71 | 68 | 63 | 63 | 63 | 63 | 63 | 63 | 0 | 25.5 | 38 | 38 | 38 | 38 | 53 | 60 | 66 | 70 | 72.5 | 72.5 | 71 | 68 | 63 | 63 | 63 | 63 | 63 | 63 | 1450
100-65-250 | 278 | 264 | 250 | 236 | 222 | 222 | 222 | 2 | 0 | 2.5 | 5 | 7.5 | 10 | 10 | 10 | 12.5 | 15 | 17.5 | 20 | 22.5 | 25 | 27.5 | 30 | 30 | 30 | 30 | 30 | 30 | 26.8 | 26.7 | 26.6 | 26.5 | 26.3 | 26.3 | 26.3 | 25.6 | 24.8 | 24.1 | 23.2 | 22.3 | 20.8 | 19.2 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 3 | 3.1 | 3.2 | 3.3 | 3.4 | 3.4 | 3.4 | 3.5 | 3.6 | 3.7 | 3.8 | 3.9 | 4 | 4.1 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 0 | 23 | 38 | 49 | 59.5 | 59.5 | 59.5 | 65.5 | 71 | 74.5 | 77 | 76.5 | 74 | 68 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 22 | 37 | 48 | 58.5 | 58.5 | 58.5 | 64.5 | 70 | 73.5 | 76 | 75.5 | 73 | 67 | 59 | 59 | 59 | 59 | 59 | 59 | 0 | 21 | 36 | 47 | 57.5 | 57.5 | 57.5 | 63.5 | 69 | 72.5 | 75 | 74.5 | 72 | 66 | 58 | 58 | 58 | 58 | 58 | 58 | 0 | 20 | 35 | 46 | 56.5 | 56.5 | 56.5 | 62.5 | 68 | 71.5 | 74 | 73.5 | 71 | 65 | 57 | 57 | 57 | 57 | 57 | 57 | 0 | 18 | 33 | 44 | 54.5 | 54.5 | 54.5 | 60.5 | 66 | 69.5 | 72 | 71.5 | 69 | 63 | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 18 | 33 | 44 | 54.5 | 54.5 | 54.5 | 60.5 | 66 | 69.5 | 72 | 71.5 | 69 | 63 | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 18 | 33 | 44 | 54.5 | 54.5 | 54.5 | 60.5 | 66 | 69.5 | 72 | 71.5 | 69 | 63 | 55 | 55 | 55 | 55 | 55 | 55 | 1450
100-65-315
100-80-160 | 182 | 173 | 164 | 155 | 146 | 146 | 146 | 2 | 0 | 2.5 | 5 | 5 | 5 | 5 | 5 | 7.5 | 10 | 12.5 | 15 | 17.5 | 20 | 22.5 | 25 | 27.5 | 28.5 | 28.5 | 28.5 | 28.5 | 10.8 | 10.75 | 10.7 | 10.7 | 10.7 | 10.7 | 10.7 | 10.65 | 10.5 | 10.3 | 9.7 | 9.1 | 8.4 | 7.6 | 6.6 | 5.4 | 4.8 | 4.8 | 4.8 | 4.8 | 2.4 | 2.5 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.7 | 2.8 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 4.3 | 5.3 | 5.6 | 5.6 | 5.6 | 5.6 | 0 | 28 | 40 | 40 | 40 | 40 | 40 | 53 | 65 | 72.3 | 74.8 | 76 | 75.5 | 73.8 | 69 | 57 | 55 | 55 | 55 | 55 | 0 | 27 | 39 | 39 | 39 | 39 | 39 | 52 | 64 | 71.3 | 74.8 | 75 | 74.5 | 72.8 | 68 | 56 | 54 | 54 | 54 | 54 | 0 | 26 | 38 | 38 | 38 | 38 | 38 | 51 | 63 | 70.3 | 72.8 | 74 | 73.5 | 71.8 | 67 | 55 | 53 | 53 | 53 | 53 | 0 | 25 | 37 | 37 | 37 | 37 | 37 | 50 | 62 | 69.3 | 71.8 | 73 | 72.5 | 70.8 | 66 | 54 | 52 | 52 | 52 | 52 | 0 | 24 | 36 | 36 | 36 | 36 | 36 | 49 | 61 | 68.3 | 70.8 | 72 | 71.5 | 69.8 | 65 | 53 | 51 | 51 | 51 | 51 | 0 | 24 | 36 | 36 | 36 | 36 | 36 | 49 | 61 | 68.3 | 70.8 | 72 | 71.5 | 69.8 | 65 | 53 | 51 | 51 | 51 | 51 | 0 | 24 | 36 | 36 | 36 | 36 | 36 | 49 | 61 | 68.3 | 70.8 | 72 | 71.5 | 69.8 | 65 | 53 | 51 | 51 | 51 | 51 | 1450
125-80-400 | 438 | 416 | 394 | 372 | 350 | 350 | 350 | 2 | 0 | 5 | 7 | 7 | 7 | 7 | 7 | 10 | 15 | 20 | 25 | 30 | 35 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 66.5 | 66.5 | 66.3 | 66.3 | 66.3 | 66.3 | 66.3 | 66 | 64.9 | 62.8 | 60 | 56.3 | 48 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 0.9 | 0.93 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.97 | 1 | 1.1 | 1.2 | 1.4 | 1.7 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 28 | 30 | 30 | 30 | 30 | 30 | 39.5 | 51 | 56.5 | 60.5 | 63 | 59 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 0 | 27.5 | 29.5 | 29.5 | 29.5 | 29.5 | 29.5 | 39 | 50 | 55.5 | 59.5 | 62 | 58 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 0 | 26.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 38 | 49 | 54 | 58 | 60.5 | 56.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 0 | 26 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 37 | 48 | 53.5 | 56.5 | 58.5 | 55 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 25 | 27 | 27 | 27 | 27 | 27 | 36 | 47 | 52.5 | 55.5 | 57.5 | 54 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 0 | 25 | 27 | 27 | 27 | 27 | 27 | 36 | 47 | 52.5 | 55.5 | 57.5 | 54 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 0 | 25 | 27 | 27 | 27 | 27 | 27 | 36 | 47 | 52.5 | 55.5 | 57.5 | 54 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1450
125-100-200 | 228 | 217 | 205 | 194 | 182 | 182 | 182 | 2 | 0 | 5 | 10 | 10 | 10 | 10 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 55 | 55 | 55 | 55 | 17 | 16.9 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.7 | 16.6 | 16.3 | 15.7 | 15 | 14.2 | 13.2 | 11.6 | 10 | 10 | 10 | 10 | 10 | 2 | 2.1 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 3 | 4 | 6 | 6 | 6 | 6 | 6 | 0 | 28 | 48 | 48 | 48 | 48 | 48 | 60 | 71 | 78 | 82 | 84 | 84 | 82 | 78 | 70 | 70 | 70 | 70 | 70 | 0 | 27.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 59 | 70 | 77 | 81 | 83 | 83 | 81 | 77 | 69 | 69 | 69 | 69 | 69 | 0 | 27 | 47 | 47 | 47 | 47 | 47 | 58 | 69 | 76 | 80 | 82 | 82 | 80 | 76 | 68 | 68 | 68 | 68 | 68 | 0 | 26 | 46 | 46 | 46 | 46 | 46 | 56 | 67 | 74 | 78 | 80 | 80 | 78 | 74 | 66 | 66 | 66 | 66 | 66 | 0 | 25 | 45 | 45 | 45 | 45 | 45 | 54 | 65 | 72 | 76 | 78 | 78 | 76 | 72 | 64 | 64 | 64 | 64 | 64 | 0 | 25 | 45 | 45 | 45 | 45 | 45 | 54 | 65 | 72 | 76 | 78 | 78 | 76 | 72 | 64 | 64 | 64 | 64 | 64 | 0 | 25 | 45 | 45 | 45 | 45 | 45 | 54 | 65 | 72 | 76 | 78 | 78 | 76 | 72 | 64 | 64 | 64 | 64 | 64 | 1450
125-100-250
125-100-315 | 342 | 325 | 308 | 291 | 274 | 274 | 274 | 2 | 0 | 5 | 10 | 10 | 10 | 10 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 57 | 57 | 57 | 57 | 40.3 | 40.2 | 40.1 | 40.1 | 40.1 | 40.1 | 40.1 | 40 | 39.8 | 39.5 | 39.2 | 38.5 | 37.5 | 36 | 33.8 | 31.8 | 30 | 30 | 30 | 30 | 1.7 | 1.8 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 2 | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.8 | 3.3 | 3.8 | 4 | 4 | 4 | 4 | 0 | 23 | 40 | 40 | 40 | 40 | 40 | 53.8 | 63.8 | 68.3 | 73.8 | 77.3 | 79 | 79.3 | 79 | 76 | 75 | 75 | 75 | 75 | 0 | 22.5 | 39 | 39 | 39 | 39 | 39 | 52.8 | 62.8 | 67.3 | 72.8 | 76.3 | 78 | 78.3 | 78 | 75 | 74 | 74 | 74 | 74 | 0 | 22 | 38 | 38 | 38 | 38 | 38 | 51.8 | 61.8 | 66.3 | 71.8 | 75.3 | 77 | 77.3 | 77 | 74 | 73 | 73 | 73 | 73 | 0 | 21.5 | 37 | 37 | 37 | 37 | 37 | 50.8 | 60.8 | 65.3 | 70.8 | 74.3 | 76 | 76.3 | 76 | 73 | 72 | 72 | 72 | 72 | 0 | 21 | 36 | 36 | 36 | 36 | 36 | 59.8 | 59.8 | 64.3 | 69.8 | 73.3 | 75 | 75.3 | 75 | 72 | 71 | 71 | 71 | 71 | 0 | 21 | 36 | 36 | 36 | 36 | 36 | 59.8 | 59.8 | 64.3 | 69.8 | 73.3 | 75 | 75.3 | 75 | 72 | 71 | 71 | 71 | 71 | 0 | 21 | 36 | 36 | 36 | 36 | 36 | 59.8 | 59.8 | 64.3 | 69.8 | 73.3 | 75 | 75.3 | 75 | 72 | 71 | 71 | 71 | 71 | 1450
125-100-400 | 438 | 416 | 394 | 372 | 350 | 350 | 350 | 2 | 0 | 5 | 10 | 10 | 10 | 10 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 57 | 57 | 57 | 57 | 66.8 | 66.5 | 66.3 | 66.3 | 66.3 | 66.3 | 66.3 | 66.1 | 65.9 | 65.7 | 64.3 | 63.8 | 62 | 60.3 | 58.2 | 55.8 | 54.8 | 54.8 | 54.8 | 54.8 | 2 | 2.05 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 2.8 | 2.9 | 3 | 3.1 | 3.1 | 3.1 | 3.1 | 0 | 23 | 33 | 33 | 33 | 33 | 33 | 48 | 55 | 61 | 66 | 68 | 69.5 | 71 | 71 | 69.3 | 68 | 68 | 68 | 68 | 0 | 22 | 32 | 32 | 32 | 32 | 32 | 46.5 | 53.5 | 59.5 | 64.5 | 66.5 | 68.5 | 69.5 | 69.5 | 68.5 | 66.5 | 66.5 | 66.5 | 66.5 | 0 | 21 | 31 | 31 | 31 | 31 | 31 | 45.5 | 52.5 | 58.5 | 63.5 | 65.5 | 67.5 | 68.5 | 68.5 | 67.5 | 65.5 | 65.5 | 65.5 | 65.5 | 0 | 20 | 30 | 30 | 30 | 30 | 30 | 44.5 | 51.5 | 57.5 | 62.5 | 64.5 | 66.5 | 67.5 | 67.5 | 66.5 | 65 | 65 | 65 | 65 | 0 | 19 | 29 | 29 | 29 | 29 | 29 | 43.5 | 50.5 | 56.5 | 61.5 | 63.5 | 65.5 | 66.6 | 66.5 | 65.5 | 64 | 64 | 64 | 64 | 0 | 19 | 29 | 29 | 29 | 29 | 29 | 43.5 | 50.5 | 56.5 | 61.5 | 63.5 | 65.5 | 66.6 | 66.5 | 65.5 | 64 | 64 | 64 | 64 | 0 | 19 | 29 | 29 | 29 | 29 | 29 | 43.5 | 50.5 | 56.5 | 61.5 | 63.5 | 65.5 | 66.6 | 66.5 | 65.5 | 64 | 64 | 64 | 64 | 1450
125-100-500 | 547 | 520 | 492 | 465 | 437 | 437 | 437 | 2.2 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 15 | 20 | 25 | 30 | 35 | 40 | 46 | 54 | 59 | 62 | 68 | 72 | 105 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104.3 | 104 | 103.8 | 102.8 | 101.8 | 99.8 | 97 | 93 | 88.8 | 81.3 | 76 | 72.8 | 66 | 60 | 1.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.42 | 1.45 | 1.5 | 1.55 | 1.6 | 1.65 | 1.7 | 1.9 | 2 | 2.35 | 2.7 | 3.2 | 4 | 0 | 28 | 28 | 28 | 28 | 28 | 28 | 30 | 40 | 45 | 50 | 54 | 56 | 57 | 58.5 | 57 | 56 | 54 | 50 | 45 | 0 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 29.5 | 39.5 | 44.5 | 49.5 | 53.5 | 55.5 | 56.5 | 58 | 56.5 | 55.5 | 53.5 | 49.5 | 43.5 | 0 | 26 | 26 | 26 | 26 | 26 | 26 | 28 | 38 | 43 | 48 | 52 | 54 | 55 | 56.5 | 55 | 54 | 52 | 48 | 42 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 27 | 37 | 42.5 | 47.5 | 51.5 | 53.5 | 54.5 | 56 | 54.5 | 53.5 | 51.5 | 47.5 | 41.5 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 26 | 36 | 41.5 | 46.5 | 50.5 | 52.5 | 53.5 | 55 | 53.5 | 52.5 | 50.5 | 46.5 | 40.5 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 26 | 36 | 41.5 | 46.5 | 50.5 | 52.5 | 53.5 | 55 | 53.5 | 52.5 | 50.5 | 46.5 | 40.5 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 26 | 36 | 41.5 | 46.5 | 50.5 | 52.5 | 53.5 | 55 | 53.5 | 52.5 | 50.5 | 46.5 | 40.5 | 1450
150-125-250 | [8 empty] | NPSH 20: 100
150-125-315 | 342 | 325 | 308 | 291 | 274 | 274 | 274 | 2.2 | 0 | 10 | 20 | 30 | 30 | 30 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 105 | 105 | 105 | 105 | 105 | 105 | 40.4 | 40.3 | 40.2 | 40.1 | 40.1 | 40.1 | 40.1 | 40 | 39.3 | 38 | 36 | 33.3 | 30.3 | 26 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 2.6 | 2.7 | 2.9 | 3 | 3 | 3 | 3 | 3.1 | 3.2 | 3.3 | 3.4 | 3.5 | 3.7 | 4 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 0 | 33 | 53 | 66 | 66 | 66 | 66 | 74 | 80 | 84.3 | 86.1 | 84.8 | 82.8 | 74.8 | 69 | 69 | 69 | 69 | 69 | 69 | 0 | 32 | 52 | 65 | 65 | 65 | 65 | 73 | 79 | 83.3 | 85.1 | 83.8 | 81.8 | 73.8 | 68 | 68 | 68 | 68 | 68 | 68 | 0 | 29.7 | 49.7 | 62.7 | 62.7 | 62.7 | 62.7 | 70.7 | 76.7 | 81 | 82.8 | 81.5 | 79.5 | 71.5 | 65.7 | 65.7 | 65.7 | 65.7 | 65.7 | 65.7 | 0 | 28.4 | 48.4 | 61.4 | 61.4 | 61.4 | 61.4 | 69.4 | 75.4 | 79.7 | 81.5 | 80.2 | 78.2 | 70.2 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 64.4 | 0 | 27.1 | 47.1 | 60.1 | 60.1 | 60.1 | 60.1 | 68.1 | 74.1 | 78.4 | 80.2 | 78.9 | 76.9 | 68.9 | 63.1 | 63.1 | 63.1 | 63.1 | 63.1 | 63.1 | 0 | 27.1 | 47.1 | 60.1 | 60.1 | 60.1 | 60.1 | 68.1 | 74.1 | 78.4 | 80.2 | 78.9 | 76.9 | 68.9 | 63.1 | 63.1 | 63.1 | 63.1 | 63.1 | 63.1 | 0 | 27.1 | 47.1 | 60.1 | 60.1 | 60.1 | 60.1 | 68.1 | 74.1 | 78.4 | 80.2 | 78.9 | 76.9 | 68.9 | 63.1 | 63.1 | 63.1 | 63.1 | 63.1 | 63.1 | 1450
150-125-400 | 438 | 416 | 394 | 372 | 350 | 350 | 350 | 2 | 0 | 10 | 20 | 20 | 20 | 20 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 66 | 65.9 | 65.8 | 65.8 | 65.8 | 65.8 | 65.8 | 65.6 | 65.4 | 65.2 | 65 | 63 | 60 | 55 | 49 | 49 | 49 | 49 | 49 | 49 | 0.9 | 0.95 | 1 | 1 | 1 | 1 | 1 | 1.2 | 1.4 | 1.7 | 2 | 2.5 | 3.3 | 4.8 | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 28 | 48 | 48 | 48 | 48 | 48 | 63 | 70 | 74 | 78 | 79.5 | 80 | 77 | 70 | 70 | 70 | 70 | 70 | 70 | 0 | 27.5 | 47 | 47 | 47 | 47 | 47 | 62 | 69 | 73.5 | 78 | 79 | 79.5 | 76 | 69 | 69 | 69 | 69 | 69 | 69 | 0 | 27 | 46 | 46 | 46 | 46 | 46 | 61 | 68 | 73 | 77 | 78.5 | 79 | 75 | 68 | 68 | 68 | 68 | 68 | 68 | 0 | 26.5 | 45 | 45 | 45 | 45 | 45 | 60 | 67 | 72.5 | 76.5 | 78 | 78 | 74 | 67 | 67 | 67 | 67 | 67 | 67 | 0 | 26 | 44 | 44 | 44 | 44 | 44 | 59 | 66 | 72 | 76 | 77.5 | 77 | 73 | 66 | 66 | 66 | 66 | 66 | 66 | 0 | 26 | 44 | 44 | 44 | 44 | 44 | 59 | 66 | 72 | 76 | 77.5 | 77 | 73 | 66 | 66 | 66 | 66 | 66 | 66 | 0 | 26 | 44 | 44 | 44 | 44 | 44 | 59 | 66 | 72 | 76 | 77.5 | 77 | 73 | 66 | 66 | 66 | 66 | 66 | 66 | 1450
150-125-500 | 547 | 520 | 492 | 465 | 437 | 437 | 437 | 2 | 0 | 10 | 20 | 20 | 20 | 20 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 106 | 105.5 | 105 | 105 | 105 | 105 | 105 | 104 | 102 | 99.8 | 96.2 | 92.3 | 87.3 | 80 | 73 | 73 | 73 | 73 | 73 | 73 | 1.5 | 1.6 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.8 | 1.9 | 2 | 2.1 | 2.7 | 3.4 | 4.5 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 0 | 23 | 40 | 40 | 40 | 40 | 40 | 54 | 58 | 62 | 64.8 | 66 | 67 | 65 | 61 | 61 | 61 | 61 | 61 | 61 | 0 | 22.5 | 39 | 39 | 39 | 39 | 39 | 53 | 57.5 | 61.5 | 64.3 | 65.5 | 66.5 | 64.5 | 60.5 | 60.5 | 60.5 | 60.5 | 60.5 | 60.5 | 0 | 22 | 38.5 | 38.5 | 38.5 | 38.5 | 38.5 | 52.5 | 57 | 61 | 63.8 | 65 | 66 | 64 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 21.5 | 38 | 38 | 38 | 38 | 38 | 52 | 56.5 | 60.5 | 63.3 | 64.5 | 65.5 | 63.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 59.5 | 0 | 21 | 37 | 37 | 37 | 37 | 37 | 51 | 56 | 60 | 62.8 | 64 | 65 | 63 | 59 | 59 | 59 | 59 | 59 | 59 | 0 | 21 | 37 | 37 | 37 | 37 | 37 | 51 | 56 | 60 | 62.8 | 64 | 65 | 63 | 59 | 59 | 59 | 59 | 59 | 59 | 0 | 21 | 37 | 37 | 37 | 37 | 37 | 51 | 56 | 60 | 62.8 | 64 | 65 | 63 | 59 | 59 | 59 | 59 | 59 | 59 | 1450
200-150-315 | 342 | 325 | 308 | 291 | 274 | 274 | 274 | 2.2 | 0 | 10 | 20 | 30 | 30 | 30 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 150 | 38.35 | 38.3 | 38.25 | 38.2 | 38.2 | 38.2 | 38.2 | 38.15 | 38.1 | 38.05 | 38 | 37.8 | 37.3 | 36.8 | 35.8 | 34.3 | 32.8 | 30.5 | 27.3 | 27.3 | 4.7 | 4.8 | 4.9 | 5 | 5 | 5 | 5 | 5.1 | 5.2 | 5.3 | 5.4 | 5.5 | 5.6 | 5.7 | 5.8 | 6 | 6.3 | 6.5 | 7 | 7 | 0 | 20 | 33 | 46 | 46 | 46 | 46 | 55 | 58 | 63 | 72 | 75 | 78 | 80 | 81 | 81 | 80 | 78 | 73 | 73 | 0 | 19 | 32 | 43 | 43 | 43 | 43 | 53 | 57 | 62 | 72 | 74 | 77 | 79.5 | 80.5 | 80.5 | 78 | 77 | 72 | 72 | 0 | 18 | 31 | 40 | 40 | 40 | 40 | 51 | 55 | 60 | 70 | 73 | 76 | 79 | 80 | 80 | 76 | 75 | 70 | 70 | 0 | 17 | 30 | 38 | 38 | 38 | 38 | 50 | 54 | 59 | 68 | 72 | 75 | 77 | 78 | 78 | 74 | 73 | 67 | 67 | 0 | 16 | 29 | 35 | 35 | 35 | 35 | 47 | 51 | 56 | 65 | 70 | 73 | 75 | 77 | 77 | 72 | 70 | 65 | 65 | 0 | 16 | 29 | 35 | 35 | 35 | 35 | 47 | 51 | 56 | 65 | 70 | 73 | 75 | 77 | 77 | 72 | 70 | 65 | 65 | 0 | 16 | 29 | 35 | 35 | 35 | 35 | 47 | 51 | 56 | 65 | 70 | 73 | 75 | 77 | 77 | 72 | 70 | 65 | 65 | 1450
200-150-400 | 438 | 416 | 394 | 372 | 350 | 350 | 350 | 2.3 | 0 | 10 | 20 | 30 | 30 | 30 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 64.3 | 64.25 | 64.2 | 64.15 | 64.15 | 64.15 | 64.15 | 64.1 | 64.05 | 64 | 63.7 | 62.4 | 61.5 | 60 | 58 | 55.9 | 53 | 49.2 | 45 | 40 | 2.3 | 2.4 | 2.5 | 2.6 | 2.6 | 2.6 | 2.6 | 2.7 | 2.8 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 3.5 | 3.7 | 4 | 4.3 | 5 | 5 | 0 | 28 | 38 | 40 | 40 | 40 | 40 | 51 | 59 | 65 | 68 | 72 | 75 | 77 | 78.3 | 81 | 81.5 | 80 | 77.5 | 75 | 0 | 27 | 37 | 39 | 39 | 39 | 39 | 50 | 58 | 64 | 67 | 71 | 74 | 76 | 77.3 | 80 | 80.5 | 79 | 76.5 | 74 | 0 | 26 | 35 | 37 | 37 | 37 | 37 | 48 | 56 | 62 | 65 | 69 | 72 | 74 | 75.3 | 78 | 78.5 | 77 | 74.5 | 72 | 0 | 25 | 33 | 35 | 35 | 35 | 35 | 46 | 54 | 60 | 63 | 67 | 70 | 72 | 73.3 | 76 | 76.5 | 75 | 72.5 | 70 | 0 | 24 | 30 | 32 | 32 | 32 | 32 | 43 | 51 | 57 | 60 | 64 | 67 | 69 | 70.3 | 73 | 73.5 | 72 | 69.5 | 67 | 0 | 24 | 30 | 32 | 32 | 32 | 32 | 43 | 51 | 57 | 60 | 64 | 67 | 69 | 70.3 | 73 | 73.5 | 72 | 69.5 | 67 | 0 | 24 | 30 | 32 | 32 | 32 | 32 | 43 | 51 | 57 | 60 | 64 | 67 | 69 | 70.3 | 73 | 73.5 | 72 | 69.5 | 67 | 1450
200-150-500 | 547 | 520 | 492 | 465 | 437 | 437 | 437 | 2.2 | 0 | 20 | 25 | 30 | 30 | 30 | 30 | 35 | 55 | 65 | 77 | 85 | 95 | 100 | 110 | 115 | 135 | 145 | 155 | 175 | 100.2 | 100.1 | 100 | 99.9 | 99.9 | 99.9 | 99.9 | 99.8 | 99.7 | 99.5 | 97.5 | 97 | 95 | 93 | 91 | 89.8 | 81 | 76 | 70.3 | 58 | 2 | 1.9 | 1.9 | 2 | 2 | 2 | 2 | 2.05 | 2.15 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.8 | 3 | 3.2 | 3.5 | 4.3 | 7 | 0 | 30 | 35 | 40 | 40 | 40 | 40 | 48 | 60 | 65 | 70 | 73 | 75 | 76 | 77 | 78 | 75 | 73 | 70 | 60 | 0 | 29.5 | 34.5 | 39.5 | 39.5 | 39.5 | 39.5 | 47.5 | 59.5 | 64 | 69 | 72 | 73.5 | 74.5 | 75.5 | 76.5 | 73.5 | 71.5 | 68.5 | 59 | 0 | 29 | 34 | 39 | 39 | 39 | 39 | 47 | 59 | 63 | 68 | 70.5 | 72 | 73 | 74 | 75 | 72 | 70 | 67.5 | 58 | 0 | 28 | 33 | 38 | 38 | 38 | 38 | 46 | 58 | 62 | 67 | 69.5 | 71 | 72 | 73 | 74 | 71 | 69 | 66.5 | 57 | 0 | 27 | 37 | 37 | 37 | 37 | 37 | 45 | 56.5 | 60.5 | 65.5 | 68 | 69.5 | 70.5 | 71.5 | 72.5 | 69.5 | 67.5 | 65 | 55.5 | 0 | 27 | 37 | 37 | 37 | 37 | 37 | 45 | 56.5 | 60.5 | 65.5 | 68 | 69.5 | 70.5 | 71.5 | 72.5 | 69.5 | 67.5 | 65 | 55.5 | 0 | 27 | 37 | 37 | 37 | 37 | 37 | 45 | 56.5 | 60.5 | 65.5 | 68 | 69.5 | 70.5 | 71.5 | 72.5 | 69.5 | 67.5 | 65 | 55.5 | 1450
250-200-200
250-200-250
250-200-315
250-200-400 | 438 | 416 | 394 | 372 | 350 | 350 | 350 | 2.2 | 0 | 25 | 50 | 50 | 50 | 50 | 50 | 75 | 100 | 125 | 150 | 175 | 200 | 225 | 250 | 260 | 260 | 260 | 260 | 260 | 63 | 62.8 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.2 | 61.9 | 61.6 | 60 | 58 | 55 | 52.3 | 44.3 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 2.1 | 2.15 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.9 | 3.3 | 4 | 4.5 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 0 | 33 | 48 | 48 | 48 | 48 | 48 | 59 | 68 | 76 | 80 | 83.5 | 85.5 | 84.5 | 80 | 77 | 77 | 77 | 77 | 77 | 0 | 32.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 58.5 | 67.5 | 75.5 | 79.5 | 83 | 85 | 84 | 79.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 0 | 31 | 46 | 46 | 46 | 46 | 46 | 57 | 66 | 74 | 78 | 81.5 | 83.5 | 82.5 | 78 | 75 | 75 | 75 | 75 | 75 | 0 | 29 | 44 | 44 | 44 | 44 | 44 | 55 | 64 | 72 | 76 | 79.5 | 81.5 | 80.5 | 76 | 73 | 73 | 73 | 73 | 73 | 0 | 27 | 42 | 42 | 42 | 42 | 42 | 53 | 62 | 70 | 74 | 77.5 | 79.5 | 78.5 | 74 | 71 | 71 | 71 | 71 | 71 | 0 | 27 | 42 | 42 | 42 | 42 | 42 | 53 | 62 | 70 | 74 | 77.5 | 79.5 | 78.5 | 74 | 71 | 71 | 71 | 71 | 71 | 0 | 27 | 42 | 42 | 42 | 42 | 42 | 53 | 62 | 70 | 74 | 77.5 | 79.5 | 78.5 | 74 | 71 | 71 | 71 | 71 | 71 | 1450
250-200-500 | 547 | 520 | 492 | 465 | 437 | 437 | 437 | 3 | 0 | 25 | 50 | 50 | 50 | 50 | 50 | 60 | 80 | 108 | 135 | 150 | 170 | 195 | 220 | 240 | 250 | 265 | 265 | 265 | 100.3 | 100.5 | 101 | 101 | 101 | 101 | 101 | 101.3 | 101 | 100 | 98 | 96.9 | 93.9 | 88.3 | 81.6 | 74.5 | 70 | 63 | 63 | 63 | 2.5 | 2.53 | 2.55 | 2.55 | 2.55 | 2.55 | 2.55 | 2.58 | 2.6 | 2.65 | 2.7 | 2.75 | 2.8 | 2.85 | 2.9 | 3.1 | 3.35 | 3.7 | 3.7 | 3.7 | 0 | 25 | 45 | 45 | 45 | 45 | 45 | 50 | 60 | 70 | 77 | 81 | 84 | 85 | 84 | 81 | 77 | 70 | 70 | 70 | 0 | 25 | 45 | 45 | 45 | 45 | 45 | 50 | 60 | 69 | 76 | 80 | 83 | 84 | 83 | 80 | 76 | 69 | 69 | 69 | 0 | 24 | 44 | 44 | 44 | 44 | 44 | 49 | 59 | 67.5 | 74.5 | 78.5 | 81.5 | 82.5 | 81.5 | 78.5 | 74.5 | 67.5 | 67.5 | 67.5 | 0 | 23 | 43 | 43 | 43 | 43 | 43 | 48 | 58 | 65 | 72 | 76 | 79 | 80 | 79 | 76 | 72 | 65 | 65 | 65 | 0 | 22 | 42 | 42 | 42 | 42 | 42 | 47 | 56.5 | 63 | 70 | 74 | 77 | 78 | 77 | 74 | 70 | 63 | 63 | 63 | 0 | 22 | 42 | 42 | 42 | 42 | 42 | 47 | 56.5 | 63 | 70 | 74 | 77 | 78 | 77 | 74 | 70 | 63 | 63 | 63 | 0 | 22 | 42 | 42 | 42 | 42 | 42 | 47 | 56.5 | 63 | 70 | 74 | 77 | 78 | 77 | 74 | 70 | 63 | 63 | 63
300-250-250 | 278 | 264 | 250 | 236 | 222 | 222 | 222 | 3 | 0 | 35 | 70 | 70 | 70 | 70 | 70 | 100 | 113 | 148 | 180 | 205 | 215 | 240 | 270 | 295 | 315 | 350 | 350 | 350 | 28 | 27.5 | 27 | 27 | 27 | 27 | 27 | 26.2 | 25.5 | 24.7 | 23.8 | 23 | 21.5 | 21.2 | 19.7 | 17.4 | 16.3 | 14 | 14 | 14 | 2.8 | 2.85 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.95 | 2.98 | 3.05 | 3.13 | 3.18 | 3.2 | 3.35 | 3.5 | 3.7 | 3.9 | 4.5 | 4.5 | 4.5 | 0 | 25 | 38 | 38 | 38 | 38 | 38 | 48 | 58 | 65 | 70 | 75 | 78 | 81 | 82 | 81 | 78 | 75 | 75 | 75 | 0 | 24 | 37 | 37 | 37 | 37 | 37 | 47 | 57 | 64 | 69 | 74 | 77 | 80 | 81 | 80 | 77 | 74 | 74 | 74 | 0 | 23 | 35 | 35 | 35 | 35 | 35 | 45 | 55 | 62.5 | 68.5 | 72.5 | 75.5 | 78.5 | 79.5 | 78.5 | 75.5 | 72.5 | 72.5 | 72.5 | 0 | 22 | 33 | 33 | 33 | 33 | 33 | 43 | 53 | 60 | 66 | 70 | 73 | 76 | 77 | 76 | 73 | 70 | 70 | 70 | 0 | 21 | 31 | 31 | 31 | 31 | 31 | 41 | 51 | 58 | 64 | 68 | 71 | 74 | 75 | 74 | 71 | 68 | 68 | 68 | 0 | 21 | 31 | 31 | 31 | 31 | 31 | 41 | 51 | 58 | 64 | 68 | 71 | 74 | 75 | 74 | 71 | 68 | 68 | 68 | 0 | 21 | 31 | 31 | 31 | 31 | 31 | 41 | 51 | 58 | 64 | 68 | 71 | 74 | 75 | 74 | 71 | 68 | 68 | 68 | 1480
300-250-315 | 342 | 325 | 308 | 291 | 274 | 274 | 274 | 3 | 0 | 35 | 70 | 70 | 70 | 70 | 70 | 105 | 140 | 175 | 215 | 240 | 255 | 285 | 320 | 350 | 350 | 350 | 350 | 350 | 34 | 34.3 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.3 | 34 | 33.3 | 32 | 31.2 | 30 | 28.5 | 25.5 | 23 | 23 | 23 | 23 | 23 | 3.5 | 3.55 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.7 | 3.8 | 4 | 4.2 | 4.4 | 4.6 | 5 | 5.7 | 7 | 7 | 7 | 7 | 7 | 0 | 25 | 38 | 38 | 38 | 38 | 38 | 50 | 60 | 70 | 79 | 82 | 85 | 86.5 | 85 | 81 | 81 | 81 | 81 | 81 | 0 | 24.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 49 | 59 | 69 | 78 | 81 | 83.5 | 85 | 83.5 | 79.5 | 79.5 | 79.5 | 79.5 | 79.5 | 0 | 24 | 37 | 37 | 37 | 37 | 37 | 48 | 58 | 68 | 77 | 80 | 82.5 | 84 | 82.5 | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 0 | 23 | 36 | 36 | 36 | 36 | 36 | 47 | 57 | 67 | 75 | 78 | 80.5 | 82 | 80.5 | 76.5 | 76.5 | 76.5 | 76.5 | 76.5 | 0 | 22 | 35 | 35 | 35 | 35 | 35 | 45 | 55 | 65 | 72 | 75 | 77.5 | 79 | 77.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 0 | 22 | 35 | 35 | 35 | 35 | 35 | 45 | 55 | 65 | 72 | 75 | 77.5 | 79 | 77.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 0 | 22 | 35 | 35 | 35 | 35 | 35 | 45 | 55 | 65 | 72 | 75 | 77.5 | 79 | 77.5 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | 1480
300-250-400 | 438 | 416 | 394 | 372 | 350 | 350 | 350 | 3 | 0 | 35 | 70 | 70 | 70 | 70 | 70 | 80 | 110 | 140 | 155 | 180 | 210 | 235 | 250 | 275 | 310 | 350 | 350 | 350 | 64.5 | 64 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.3 | 62.8 | 62.5 | 62.3 | 62 | 61.7 | 61.3 | 60.8 | 59.7 | 59 | 53.5 | 53.5 | 53.5 | 3.5 | 3.55 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.63 | 3.7 | 3.8 | 3.9 | 4.05 | 4.2 | 4.4 | 4.85 | 5 | 5.5 | 7 | 7 | 7 | 0 | 25 | 36 | 36 | 36 | 36 | 36 | 46 | 53 | 60 | 65 | 70 | 75 | 79 | 81 | 84 | 85 | 84 | 84 | 84 | 0 | 24.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 45.5 | 52.5 | 59.5 | 64.5 | 69.5 | 74.5 | 78.5 | 80.5 | 83.5 | 84.5 | 83.5 | 83.5 | 83.5 | 0 | 24 | 35 | 35 | 35 | 35 | 35 | 45 | 52 | 59 | 64 | 69 | 74 | 78 | 79.5 | 82.5 | 83 | 82.5 | 82.5 | 82.5 | 0 | 23 | 34 | 34 | 34 | 34 | 34 | 44 | 51 | 58 | 63 | 68 | 73 | 76.5 | 78.5 | 80.5 | 81 | 80.5 | 80.5 | 80.5 | 0 | 22 | 33 | 33 | 33 | 33 | 33 | 43 | 50 | 57 | 62 | 67 | 72 | 75 | 76.5 | 78.5 | 79 | 78.5 | 78.5 | 78.5 | 0 | 22 | 33 | 33 | 33 | 33 | 33 | 43 | 50 | 57 | 62 | 67 | 72 | 75 | 76.5 | 78.5 | 79 | 78.5 | 78.5 | 78.5 | 0 | 22 | 33 | 33 | 33 | 33 | 33 | 43 | 50 | 57 | 62 | 67 | 72 | 75 | 76.5 | 78.5 | 79 | 78.5 | 78.5 | 78.5 | 1450
300-250-500 | 547 | 520 | 492 | 465 | 437 | 437 | 437 | 3 | 0 | 50 | 100 | 100 | 100 | 100 | 100 | 120 | 160 | 190 | 240 | 260 | 280 | 330 | 380 | 400 | 410 | 430 | 450 | 450 | 97 | 96.8 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.4 | 96 | 94.5 | 91 | 88.8 | 85.6 | 78.8 | 67.3 | 62.3 | 59 | 53 | 46 | 46 | 2.45 | 2.5 | 2.65 | 2.65 | 2.65 | 2.65 | 2.65 | 2.7 | 2.8 | 2.9 | 3 | 3.1 | 3.2 | 3.3 | 3.8 | 4 | 4.8 | 5.8 | 7 | 7 | 0 | 32 | 45 | 45 | 45 | 45 | 45 | 55 | 65 | 73 | 78 | 81 | 83 | 84.5 | 83 | 81 | 78 | 73 | 70 | 70 | 0 | 31.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 54.5 | 64.5 | 72 | 77 | 80 | 82 | 83 | 81.5 | 79.5 | 76.5 | 71.5 | 68.5 | 68.5 | 0 | 31 | 44 | 44 | 44 | 44 | 44 | 54 | 64 | 71 | 76 | 78 | 80.5 | 81.5 | 80 | 78 | 75 | 70 | 67 | 67 | 0 | 30 | 43 | 43 | 43 | 43 | 43 | 53 | 63 | 70 | 75 | 77 | 78 | 79.5 | 78 | 76 | 73 | 68 | 65 | 65 | 0 | 29 | 41 | 41 | 41 | 41 | 41 | 51 | 61 | 68 | 72.5 | 74 | 75 | 76.5 | 75 | 73 | 70 | 65 | 62 | 62 | 0 | 29 | 41 | 41 | 41 | 41 | 41 | 51 | 61 | 68 | 72.5 | 74 | 75 | 76.5 | 75 | 73 | 70 | 65 | 62 | 62 | 0 | 29 | 41 | 41 | 41 | 41 | 41 | 51 | 61 | 68 | 72.5 | 74 | 75 | 76.5 | 75 | 73 | 70 | 65 | 62 | 62 | 1450
350-300-400 | 438 | 416 | 394 | 372 | 350 | 350 | 350 | 3 | 0 | 60 | 100 | 140 | 140 | 140 | 140 | 150 | 200 | 260 | 330 | 360 | 380 | 410 | 440 | 470 | 485 | 500 | 520 | 540 | 62 | 61.6 | 61 | 60.7 | 60.7 | 60.7 | 60.7 | 60.6 | 60.5 | 60.3 | 59.3 | 58 | 57 | 55 | 52.6 | 49.7 | 47.8 | 45 | 41 | 36 | 4.9 | 4.95 | 5 | 5.08 | 5.08 | 5.08 | 5.08 | 5.1 | 5.2 | 5.3 | 5.4 | 5.5 | 5.6 | 5.75 | 5.9 | 6.05 | 6.2 | 6.35 | 6.6 | 7 | 0 | 23 | 35 | 39 | 39 | 39 | 39 | 40 | 50 | 60 | 70 | 73 | 75 | 77 | 79 | 77 | 75 | 73 | 70 | 65 | 0 | 22.5 | 33.5 | 38 | 38 | 38 | 38 | 39 | 49 | 59 | 69 | 71.5 | 73.5 | 75 | 76 | 74 | 72 | 70 | 67 | 63 | 0 | 22 | 33 | 37 | 37 | 37 | 37 | 38 | 48 | 58 | 68 | 70 | 72.5 | 73.5 | 74 | 72 | 70 | 68 | 65 | 61 | 0 | 21 | 32 | 37 | 37 | 37 | 37 | 37 | 47 | 57 | 67 | 69 | 70.5 | 71.5 | 72 | 70 | 68 | 66 | 63 | 59 | 0 | 20 | 31 | 35 | 35 | 35 | 35 | 35 | 45 | 55 | 64 | 66 | 67 | 68 | 69 | 67 | 65 | 63 | 60 | 56 | 0 | 20 | 31 | 35 | 35 | 35 | 35 | 35 | 45 | 55 | 64 | 66 | 67 | 68 | 69 | 67 | 65 | 63 | 60 | 56 | 0 | 20 | 31 | 35 | 35 | 35 | 35 | 35 | 45 | 55 | 64 | 66 | 67 | 68 | 69 | 67 | 65 | 63 | 60 | 56 | 1480
350-300-500 | 547 | 520 | 492 | 465 | 437 | 437 | 437 | 2.63 | 0 | 60 | 100 | 140 | 140 | 140 | 140 | 150 | 210 | 260 | 300 | 350 | 400 | 460 | 510 | 540 | 540 | 540 | 540 | 540 | 103 | 102.7 | 102.6 | 102.3 | 102.3 | 102.3 | 102.3 | 102.1 | 101.8 | 101 | 99.5 | 96.8 | 92 | 85.5 | 77 | 71 | 71 | 71 | 71 | 71 | 4.9 | 4.95 | 5 | 5.08 | 5.08 | 5.08 | 5.08 | 5.1 | 5.2 | 5.3 | 5.4 | 5.5 | 5.6 | 5.9 | 6.3 | 7 | 7 | 7 | 7 | 7 | 0 | 23 | 38 | 46 | 46 | 46 | 46 | 50 | 60 | 66 | 70 | 73 | 75 | 73 | 70 | 66 | 66 | 66 | 66 | 66 | 0 | 23 | 37 | 45 | 45 | 45 | 45 | 49 | 59 | 65 | 69 | 72 | 73 | 71 | 68 | 64 | 64 | 64 | 64 | 64 | 0 | 23 | 37 | 44.5 | 44.5 | 44.5 | 44.5 | 48.5 | 58.5 | 64.5 | 68 | 70.5 | 71 | 69 | 66 | 62 | 62 | 62 | 62 | 62 | 0 | 23 | 37 | 43 | 43 | 43 | 43 | 47 | 57 | 63 | 66 | 68.5 | 69 | 67 | 64 | 60 | 60 | 60 | 60 | 60 | 0 | 22.5 | 36 | 42 | 42 | 42 | 42 | 46 | 56 | 62 | 65 | 66.5 | 67 | 65 | 62 | 58 | 58 | 58 | 58 | 58 | 0 | 22.5 | 36 | 42 | 42 | 42 | 42 | 46 | 56 | 62 | 65 | 66.5 | 67 | 65 | 62 | 58 | 58 | 58 | 58 | 58 | 0 | 22.5 | 36 | 42 | 42 | 42 | 42 | 46 | 56 | 62 | 65 | 66.5 | 67 | 65 | 62 | 58 | 58 | 58 | 58 | 58 | 1480

## Dimension
Model | Center Line (H1) | H2 | Suction | Discharge | A | F | A+F | KG | Mechanical Seal | M1 | N1 | Casing Pressure | Shaft | SS420 Shaft | Max Torque NM
50-32-160 | 132 | 160 | DN50 PN16 | DN32 PN16 | 80 | 385 | 465 | 38 | Carbon V Ceramic | 100 | 240 | 16 | 24 | 24 | 103
50-32-200 | 160 | 180 | DN50 PN16 | DN32 PN16 | 80 | 385 | 465 | 46 | Carbon V Ceramic | 100 | 240 | 16 | 24 | 32 | 285
65-40-200 | 160 | 180 | DN65 PN16 | DN40 PN16 | 100 | 385 | 485 | 48 | Carbon V Ceramic | 100 | 265 | 16 | 24 | 37 | 440
65-40-250 | 180 | 225 | DN65 PN16 | DN40 PN16 | 100 | 500 | 600 | 70 | Carbon V Ceramic | 125 | 320 | 16 | 32 | 42 | 713
65-40-315 | 200 | 250 | DN65 PN16 | DN40 PN16 | 125 | 500 | 625 | 80 | Carbon V Ceramic | 125 | 345 | 16 | 32 | 48 | 1183
65-50-160 | 132 | 160 | DN65 PN16 | DN50 PN16 | 80 | 385 | 465 | 40 | Carbon V Ceramic | 100 | 240 | 16 | 24 | 65 | 2388
80-50-200 | 160 | 200 | DN80 PN16 | DN50 PN16 | 100 | 385 | 485 | 52 | Carbon V Ceramic | 100 | 265 | 16 | 24 | 76 | 3722
80-50-250 | 180 | 225 | DN80 PN16 | DN50 PN16 | 125 | 500 | 625 | 72 | Carbon V Ceramic | 125 | 320 | 16 | 32
80-50-315 | 200 | 280 | DN80 PN16 | DN50 PN16 | 125 | 500 | 625 | 87 | Carbon V Ceramic | 125 | 345 | 16 | 32
80-65-160 | 160 | 180 | DN80 PN16 | DN65 PN16 | 100 | 385 | 485 | 46 | Carbon V Ceramic | 100 | 265 | 16 | 24
100-65-200 | 180 | 225 | DN100 PN16 | DN65 PN16 | 100 | 500 | 600 | 70 | Carbon V Ceramic | 125 | 320 | 16 | 32
100-65-250 | 200 | 250 | DN100 PN16 | DN65 PN16 | 125 | 500 | 625 | 80 | Carbon V Ceramic | 160 | 360 | 16 | 32
100-65-315 | 225 | 280 | DN100 PN16 | DN65 PN16 | 125 | 530 | 655 | 118 | Carbon V Ceramic | 160 | 400 | 16 | 42
100-65-315s | 250 | 350 | DN100 PN16 | DN65 PN16 | 125 | 520 | 645 | 158 | Carbon V Ceramic | 160 | 460 | 16 | 37
100-80-160 | 160 | 200 | DN125 PN16 | DN80 PN16 | 100 | 500 | 600 | 68 | Carbon V Ceramic | 125 | 280 | 16 | 32
125-80-400 | 280 | 355 | DN125 PN16 | DN80 PN16 | 125 | 530 | 655 | 165 | Carbon V Ceramic | 160 | 435 | 16 | 42
125-100-200 | 200 | 280 | DN125 PN16 | DN100 PN16 | 125 | 500 | 625 | 85 | Carbon V Ceramic | 160 | 360 | 16 | 32
125-100-250 | 225 | 280 | DN125 PN16 | DN100 PN16 | 140 | 530 | 670 | 126 | Carbon V Ceramic | 160 | 400 | 16 | 42
125-100-315 | 250 | 315 | DN125 PN16 | DN100 PN16 | 140 | 530 | 670 | 135 | Carbon V Ceramic | 160 | 400 | 16 | 42
125-100-400 | 280 | 355 | DN125 PN16 | DN100 PN16 | 140 | 530 | 670 | 175 | Carbon V Ceramic | 200 | 400 | 16 | 42
125-100-500 | 355 | 450 | DN125 PN16 | DN100 PN16 | 160 | 670 | 830 | 313 | Carbon V Ceramic | 200 | 500 | 16 | 48
150-125-250 | 250 | 355 | DN150 PN16 | DN125 PN16 | 140 | 530 | 670 | 140 | Carbon V Ceramic | 160 | 400 | 16 | 42
150-125-315 | 250 | 315 | DN150 PN16 | DN125 PN16 | 140 | 530 | 670 | 150 | Carbon V Ceramic | 200 | 500 | 16 | 42
150-125-400 | 315 | 400 | DN150 PN16 | DN125 PN16 | 140 | 530 | 670 | 186 | Carbon V Ceramic | 200 | 500 | 16 | 42
150-125-500 | 355 | 450 | DN150 PN16 | DN125 PN16 | 160 | 670 | 830 | 336 | Carbon V Ceramic | 200 | 550 | 16 | 48
200-150-315 | 315 | 400 | DN200 PN16 | DN150 PN16 | 160 | 670 | 830 | 222 | Carbon V Ceramic | 200 | 550 | 16 | 48
200-150-400 | 315 | 450 | DN200 PN16 | DN150 PN16 | 160 | 670 | 830 | 300 | Carbon V Ceramic | 200 | 550 | 16 | 48
200-150-500 | 500 | 500 | DN200 PN16 | DN150 PN16 | 160 | 670 | 830 | 382 | Carbon V Ceramic | 200 | 550 | 16 | 48
250-200-200 | 315 | 450 | DN250 PN16 | DN200 PN16 | 180 | 670 | 850 | 345 | Carbon V Ceramic | 200 | 550 | 16 | 48
250-200-250 | 315 | 450 | DN250 PN16 | DN200 PN16 | 180 | 885 | 1065 | 490 | Carbon V Ceramic | 200 | 550 | 16 | 65
250-200-315 | 315 | 450 | DN250 PN16 | DN200 PN16 | 180 | 670 | 850 | 277 | Carbon V Ceramic | 200 | 550 | 16 | 48
250-200-400 | 355 | 500 | DN250 PN16 | DN200 PN16 | 180 | 670 | 850 | 340 | Carbon V Ceramic | 200 | 550 | 16 | 48
250-200-500 | 400 | 580 | DN250 PN16 | DN200 PN16 | 225 | 885 | 1110 | 495 | Carbon V Ceramic | 315 | 760 | 16 | 65
300-250-250 | 355 | 560 | DN300 PN16 | DN250 PN16 | 225 | 885 | 1110 | 360 | Carbon V Ceramic | 250 | 630 | 16 | 65
300-250-315 | 355 | 500 | DN300 PN16 | DN250 PN16 | 225 | 670 | 895 | 350 | Carbon V Ceramic | 250 | 690 | 16 | 48
300-250-400 | 450 | 560 | DN300 PN16 | DN250 PN16 | 225 | 885 | 1110 | 480 | Carbon V Ceramic | 250 | 690 | 16 | 65
300-250-500 | 450 | 630 | DN300 PN16 | DN250 PN16 | 225 | 885 | 1110 | 530 | Carbon V Ceramic | 315 | 760 | 16 | 65
350-300-400 | 450 | 600 | DN350 PN16 | DN300 PN16 | 250 | 975 | 1225 | 900 | Carbon V Ceramic | 315 | 760 | 16 | 75
350-300-500 | 500 | 650 | DN350 PN16 | DN300 PN16 | 250 | 975 | 1225 | 1100 | Carbon V Ceramic | 360 | 900 | 16 | 75